Perry/Willard Wastewater Treatment

Facility Board Meeting

975 West 1000 North

Willard, Utah  84340

February 13, 2013

5:00 PM

Members Present:  Steven Pettingill, Paul Nelson, Rod Mund, Robert Beebe

Members Excused:  Bruce Howard

Others Present:  Jeff Hollingsworth, Susan Obray, Minutes Clerk

Welcome and Call to Order

Chairman Pettingill welcomed and called to order the Perry/Willard Wastewater meeting.

Approval of the March 14, 2012 Minutes

MOTION:  Paul Nelson moved to approve the December 12, 2012 Minutes. Rod Mund  seconded the motion.  All in favor.

A.        Approval of the Agenda

MOTION:  Robert Beebe moved to approve the agenda as written.  Rod Mund seconded the motion.  All in favor.

B.       Public Comments

There were no public comments.

C.	Lead Operator Items

Jeff reported on items from 12/1/12-1/31/2013

- Perry/Willard Wastewater Treatment Plant had zero permit violations or out of compliance during 2012.

- The 2012 yearly sludge report has been sent to the EPA Region VIII and DEQ.

- 716 Tons of sludge processed for the 2012 year at $7,244.35.

- When Utilities where marked for the effluent flume, Sunrise moved flume approximately 15 feet to the west.  Sunrise said there would not be an effect on future hydraulic loading of the ditch.

- Winn-911 call-out system has been resolved with a slower modem.

- Winn-911 has credited us back $955.00 on new modem.

- When testing the alarm system it has been intermittent.  The phone company cannot find a problem each time Jeff calls.  Jeff said he can hear background noise on the phone line.

- Both Reznor air exchange units keep flaming out daily.  Advanced heating who installed said this will be a constant item of maintenance.  These units primary function are to exchange air, not heat efficiently.

- Thomas & Associates designed the heating system for Sunrise

- Infinity Electric completed digester D.O. probe problem under warranty.

- ICTECH charges $185.00 for programming D.O. probes.

- 12/3/12 Flume construction started.  Now completed waiting on ultra sonic installation. The electrical will be billed directly to Sunrise.  Infinity will be out in the next two weeks weather permitting.

- New drive unit delivered for IFAS system. (Waiting for Dave from Westech).

- 12/14/12 House water pump stuck on during the night.  Rebooting cleared the problem.

- 12/24/12 Loveland’s gate is closed running Perry/Willard Wastewater Treatment Plant discharge on Loveland’s property.

- The plant has biologically changed.  Had Polydyne retest our Polymer and changed to a new product, there will not be a cost increase.

- 1/8/13 Ordered $950 of lab sample product.

- 1/9/13 Ford F550 into dealer for oil leaks (dip stick tube broke).

- Influent pump P431 keep failing.  Turned VFD AMP settings up to 115%.  No problems since.

- Influent pump P432 failed.  Turned VFD AMP settings up 115%.  No problems.

This was approved by Gorman Rep.

- Pump issue might be caused by grit coming into pump basin.

- 1/22/13 All piping in Ops.  Building froze.  Replace two cracked parts on the polymer injection system. (cost $2,000 dollars).

- 1/22/13 Vactor truck went to Perry City

- 1/24/13 Digester flood alarm went off.  Ventilation system was brining moisture in.  Melted ice and pumped vault out.

- Still having to replace nuts on IFAS aerator system.

- Two call outs/ flood alarm, influent pump station.

- 63 tons of sludge processed in January.

Jeff reported that Jared Quayle is doing a good job. Shows up on time, does what is expected of him every day.   Jared is studying  his Rural water manual.  He passed his CDL test and needs to do the driving test.

Robert Beebe asked if the weir is complete.  Jeff stated the weir is complete, and he is waiting for Infinity to come and do the electrical.  Jeff stated that Sunrise Engineering will be billed for this. Jeff stated that Sunrise moved flume approximately 15 feet to the west.  Sunrise said there would not be an effect on future hydraulic loading of the ditch.  Jeff stated on 12/3/12 the Flume construction started.  Now completed waiting on ultra sonic installation. The electrical will be billed directly to Sunrise.  Infinity will be out in the next two weeks weather permitting.

D.	Construction progress updates by Sunrise Engineering

The Sunrise Engineering representative was not present.

E.	Items to be Purchased

Nothing to purchase.

Rod Mund asked about the Questar Bill.  He said one gas bill is $13.00 and the other is

$130.00 for November and December.  Chairman Pettingill stated that this is the bill for                          the previous cycle.  He said the higher bill will probably come in March for January and February.  Jeff stated he did not run the furnace in December.  Jeff stated he is trying to keep the furnace at 35 degrees. Jeff stated that the 6 inch line to the digester froze up.  Robert Beebe asked if they could call a couple of plumbers to come and get it fixed. Jeff said they wanted to put electric heat in at the beginning.   He said he has talked to Jeremy over at Advanced Heating they have not come back for a service call.  He said the thermostats in the building do not do anything.  He said he did not think the damper is closing down enough and pulls the flame out.  Jeff thought the radiant heat would be the simplest way.  Jeff stated as soon as he could get water he starting running water on everything he could to break it loose.  Jeff stated the furnace not even circulating the air.

Chairman Pettingill suggested Jeff talk to Thomas and Associates, they are the engineering company that designed it for Sunrise.

F.	Board Member Items

Paul Nelson stated that he is concerned about the heating issue.

G.	Call Outs

Two call outs.

H.	Final Payment for South Outfall

Chairman Pettingill stated that there is a copy of the document for final payment on the

South Outfall.  He said that this is a disbursement request is for $17,599.80.  He said that

A reimbursement schedule is attached (exhibit B-3) $1,600.00 for New Castle Homes

Inc. for manhole modifications and for Sunrise Engineering for $2,500 for design and

Construction administration of manhole modifications.  Robert Beebe stated he did not

Have a problem paying New Castle Homes, but would like to see a breakdown of the

Charges for the work Sunrise Engineering did.  Paul stated that it cost $1,600 to fix the

Manholes and $2,500 to engineer it.  Rod Mund stated that the current budget is $19,300,

Previously disbursed was $16,800 and $2,500 disbursed at this request which makes a

Total of $19,300 that is in the current budget.  All board members felt that Sunrise

Engineering should submit a detailed breakdown.  Jeff stated that the gate leaks.

MOTION:  Rod Mund moved to direct Chairman Pettingill to sign the disbursement

Request form in the amount of $15,099.80, withholding $2,500 from the payment for

Construction Administration for Sunrise Engineering pending clarification on the bill

from them.  Robert Beebe seconded the motion.  All in favor.

- Payment Approval

Board Members signed the payment approval sheet.

J.	Discussion and/or Motion regarding Check Signing Agreement

Steve stated that there is a Resolution 13-01 adopting a check approval process.

Rod Mund asked if it was anticipated that the board only meet every two months.

Chairman Pettingill stated no it is not anticipated that we meet every two months.

He stated looking at section 1 3, 4, and 5, it is what they are doing now.  Chairman

Pettingill stated the bills are being paid and on time.  The board will take this under

advisement.

MOTION:  Robert Beebe moved to table Resolution 13-01, Check Approval Process

And take it under advisement for a future meeting.  Paul Nelson seconded the motion.

All in favor.

4.	Action Taken

None

5.	Closed Session (if needed)

None

6.	Items for next agenda (if any)

Review Resolution 13-01 Check Approval Process

7.	Adjournment

MOTION:  Rod Mund moved to adjourn.  Robert Beebe seconded the motion.  All in favor.