Perry/Willard Wastewater Treatment

Facility Board Meeting

975 West 1000 North

Willard, Utah  84340

November 14, 2012

5:00 PM

Members Present:  Steven Pettingill, Paul Nelson, Bruce Howard, Rod Mund

Members Absent:  Robert Beebe

Others Present:  Jeff Hollingsworth, Shanna Johnson, Minutes Clerk

Welcome and Call to Order

Chairman Pettingill welcomed and called to order the Perry/Willard Wastewater meeting.

Approval of the March 14, 2012 Minutes

MOTION:  Rod Mund moved to approve the October 10, 2012 Minutes. Bruce Howard   seconded the motion.  All in favor.

Approval of the Agenda

MOTION:  Bruce Howard moved to approve the agenda items.  Rod Mund seconded the motion.  All in favor.

Public Comments

No public comments.

Lead Operator Items

- 10/1/2 Jared Quayle’s first day

- Westech working gearboxes and seals.  S.E.W working seals for Westech

- 10/5/2012 Mike Grimes contacted to bring contract for emergency bypass

- 10/9/2012 Loveland’s gate not holding water. Contacted Allied and Sunrise

- 10/10/2012 Diverted WWTP for Allied to repair leaks on Loveland gate

- Radar still giving high level alarms contacted infinity electric

- 10/11/2012 State DMR sent

- 10/15/2012 First day of flow to Loveland’s gate still leaking contacted Sunrise

- 10/16/2012 State of Utah out sampling.  Call out 1749 power loss.  Plant back up at 2050.

- 10/17/2012 Allied reseeding properties.  State of Utah out sampling reaceway.

- 10/18/2012 Discharge pipe stopped flowing on Loveland’s and was coming out on Heinig’s property.  Videoed the flow and reported to Sunrise.  Opened gate to stop the flooding on Heinig’s.  State of Utah sampling raceway.

- 10/19/2012 Loveland’s called about water

- 10/21/2012 Westech called and gears are not in change out

- 10/22/2012 Sunrise out to look at the ditch

- 10/24/2012 Thatcher delivered Alum.  Sent video of water flow on Heinig’s property to Bart at Allied.

- 10/25/2012 Shanna gave ok to pay Jared for his phone bill of $22.00 a month.  Auto dialer at plant was setup and verified it works.

- 10/29/2012 Perry used Vactor truck

- 10/30/2012 Sent e-mail to Mark Davidson on Discharge ditch.  Jeremy from Sunrise contacted Jeff and said it was warranty work for Allied.

- 10/31/2012 Mark Davidson called on the ditch

- Phosphorous was .55 for this month

There was 50 tons of sludge processed for October.

Construction progress by John Roberts with Sunrise Engineering

No Sunrise representative present.

Items to be Purchased

2 barrels Polymer was ordered on 11/14/2012

Board Member Items

Bruce Howard stated that he and Mayor Nelson the Willard Spur meet with the state.  He said based on the state sampling and Jeff’s reports we are cleaning up the Willard Spur with the discharge.  He said we are taking the phosphorus out of the spur with our alum treatment.

Call Outs

Jeff had 3 call outs and was turned into Shanna for payment from Perry City.

Pipeline Discussion

Steve Pettingill stated he talked with Jeremy from Sunrise Engineering. He said they went out and measured the pipe at Loveland’s.  He said they are going to lower the box 1 foot on the Loveland’s property, and raise the box in Heinig by 2 feet. He said Mitch Hancock is going to come out and do the work. Chairman Pettingill stated that there is some water damage on the Heinig property.  He said that this will have to reseed the affected area.  He said Jeremy told him that there needs to have a motion and call the contract complete with Allied and pay them and this will be warranty work that they will come back and do .  He said in conjunction with fixing this they want to install a discharge flume.  The cities will have to pay $6,000 for the flume ($4,000 for Perry and $2,000 for Willard).  The state will pay for the manhole modifications.

HHe

MOTION:   Bruce Howard moved to close out the contract with Allied Construction except for the warranty work and to hire Mitch Hancock to do the manhole modifications.   Steve stated he would like to add to the motion to readdress of the grade on the pipeline where it has sunk and fixing the 36 inch valve. Bruce Howard stated the motion stands. Paul Nelson seconded the motion.  All in favor.

Payment Approval

Board Members signed the payment approval.

Discussion regarding Sunrise Engineering Final Payment

Jeff stated that $6,000 was agreed on for the flume total.  He said the bid came back at $18,000.  Jeff said it was ordered last Friday.

Discussion Regarding the 2013 Meeting Schedule

MOTION: Bruce Howard moved to accept the 2013 meeting schedule for the Perry/Willard Wastewater Treatment Plant.  Rod Mund seconded the motion.  All in favor.

Closed Session

None

Items for Next Agenda

None

Adjournment

MOTION:  Bruce Howard moved to adjourn.  Paul Nelson seconded the motion.  All in favor.