Perry/Willard Wastewater Treatment

Facility Board Meeting

975 West 1000 North

Willard, Utah  84340

October 10, 2012

5:00 PM

Members Present:  Steven Pettingill, Paul Nelson, Bruce Howard, Robert Beebe, Rod Mund

Others Present:  Jeff Hollingsworth, John Roberts, Sunrise Engineering; Shanna Johnson, Minutes Clerk

Welcome and Call to Order

Chairman Pettingill welcomed and called to order the Perry/Willard Wastewater meeting.

Approval of the March 14, 2012 Minutes

MOTION:  Bruce Howard moved to approve the August 8, 2012 Minutes.  Robert Beebe seconded the motion.  All in favor.

Approval of the Agenda

MOTION:  Bruce Howard moved to approve the agenda items.  Robert Beebe seconded the motion.  All in favor.

Public Comments

No public comments.

Lead Operator Items

- Westech warranty will not cover gears. Will sell gears to us at cost, and provide the labor to replace the old gears. Scheduled October 22nd.

- Interviewed applicants to assist Jeff in operating the plant and hired Jared Quayle

- Yearly required metals sample and testing report has been sent to DWQ.

- Passed our quarterly Bio monitoring for acute and chronic discharge conditions (fathead minnows)

- Rain for Rent has no fee for on call bypass part of the plant process in emergency conditions.  We will need to sign a contract for their services.

- We are out of our warranty on the UV disinfecting lamps.  There are 80 lamps in our system; replacement costs are $284.00 per lamp.  The lamps are still disinfecting fine but we should now start budgeting for new lamps.

- We will need to order Alum by the end f the year. (@ 24 tons per truck load at a cost of $425.00 per ton)

- We are current with Central Weber on sludge disposal

- PWRWWTP processed 50 tons on sludge for month

- Contacted Kurt Shaw at Huber on the press problems.   Followed up with an e-mail no action yet.

- The backup generator has 1228 gallons of fuel for winter.

- Mailed letter to Matt Garn at DEQ as he requested on 002 discharge out fall.

- Pulled gearbox on South IFAS system and placed on north side until Westech has a replacement.

- UV system failed on level sensor 9/19/12 (called out)

- Currently running 38 gallons of Alum for phosphorus removal.  This is the correct dosing for our plant.  If the phosphorus is not removed from the system, mixer will need to be added to the system.

Jeff stated the wet well is still giving him trouble.  He said he thinks he has lost the motor on the exhaust fan on the wet well, and having trouble with two other gages.

Construction progress by John Roberts with Sunrise Engineering

John Roberts stated that Allied Construction will be at the plant before the 15th to fix the seal on the head gate in the south discharge pipe line.  The covering over the south discharge pipe will have to be seeded before it is flooded, they will be here the first of next week to do the work.  The flume bid came back from Allied at $18,000 and Sunrise Engineering thought it was a little steep.  Mr. Roberts said two other contractors that have given them bids, Mitch Hancock and Great Basin Development.  Mr. Roberts said if he could hire a contractor he would pick Great Basin Development because they have always been straight forward and honest with him.  He said that Sunrise Engineering has ordered the weir.

Items to be Purchased

Lab supplies

Steve stated he felt that Jeff should have 10% of lamps on the shelf.  Jeff stated that would be 8 lamps and he has 7 lamps on the shelf now.  Steve suggested making a notation to implement money in next year’s budget for extra lamps.

Board Member Items

Steve stated he has had a discussion with Mr. Loveland regarding the water use.  He does not yet have a signed agreement but expects one in a few days.  The Duck Club signed an agreement and has been filed with Perry City and the Plant.  He said Matt Garn called and asked about the agreement.  Bruce stated he would like a copy of the agreement. Rod Mund wanted to ensure proper paperwork was submitted for water discharge rights.

Call Outs

None

Discussion about the gate on the pipe line

This item was talked about previously in the meeting.

Payment Approval

All board members present signed the payment approval sheet.

Discussion

None

Action Taken

None

Closed Session(if needed)

None

Adjournment

MOTION:  Bruce Howard moved to adjourn.  Rod Mund seconded the motion.  All in favor.